Bio-GATE

Tag Number/Serial Number/Customer Provided #

Operations and Maintenance Manual

PLANT NAME

LOCATION

Specification Section XX XX XX

Engineer of Record: XXXX

Revision X

MONTH YEAR

Table of Contents

Contact Information	4

1.	Scope of Supply	5

1.1	Equipment Data	5

1.2	Special Tools	5

1.3	Field Service	5

1.4	Scope Exclusions	5

1.5	Spare Parts	5

2.	Safety Precautions	6

3.	Delivery, Handling, and Storage	7

3.1	Upon Equipment Arrival	7

3.2	General Handling and Storage Information	7

3.2.1	Avoiding Cross-Contamination Between Materials	7

3.3	Storage	9

3.3.1	General Requirements for Indoor Storage	10

3.3.2	General Requirements for Outdoor Storage	10

3.3.3	Gear Units	11

3.3.4	Electric Motors and Actuators	12

4.	Installation Instructions	14

4.1	Before Installation	14

4.2	Detailed Installation Instructions	16

5.	Operating Procedures	17

5.1	General Equipment Operation	17

5.2	Startup	17

5.3	Shutdown	18

6.	Maintenance, Lubrication, & Troubleshooting	19

6.1	Preventative Maintenance	19

6.2	Corrective Maintenance	20

6.2.1	Seal Replacement	20

6.3	Lubrication	21

6.4	Troubleshooting	21

7.	Policies	23

7.1	Warranty	23

7.2	Liability	23

7.3	Returns	23

7.4	Delivery	23

7.5	Thread Lubricant Information	24

7.6	Standard Erecting Practices	24

Table of Figures

No table of figures entries found.

List of Tables

Table 1. Typical Bolt Torque Chart	15

Table 2. Bio-GATE Preventative Maintenance	19

Table 3. Bio-GATE Troubleshooting	21

List of Appendices

Appendix A: Catalog Cuts

Appendix B: Equipment Drawings

Appendix C: Calculations

Appendix D: Startup Reports

Appendix E: Controls

Appendix F: O&M Revision History

Local JMS Representative:

Rep Name

Company Name

Company Address

City, State Zip

(XXX)XXX-XXXX

JMS Project Manager:

PM Name Here

Jim Myers & Sons, Inc.

PO Box 38778

Charlotte, NC 28278

Phone: (704)554-8397

Fax: (704)554-9113

Contact Information

For general inquiries regarding field services, contact custsvc@jmsequipment.com.

For general inquiries regarding aftermarket parts, contact AMP@jmsequipment.com.

# Scope of Supply

JMS is supplying X (Number) X (description from scope), also referred to herein as (a) “Bio-GATE”(s). INSERT ANYTHING ELSE FROM SCOPE OF SUPPLY FROM APPROVED SUBMITTAL. [Make sure that slide gate and associated actuator are both included]

## Equipment Data

Please refer to the drawings and calculations provided in Appendix B: Equipment Drawings and Appendix C: Calculations respectively for detailed equipment parameters.

## Special Tools

While no special tools are required for working with the Bio-GATE, care should be taken to avoid cross-contamination between carbon steel originating from sources outside the immediate system and stainless-steel components when installing, maintaining, or otherwise working with the equipment or components. Please refer to the additional information about carbon steel contamination provided in Section 3.2.1 - Avoiding Cross-Contamination Between Materials.

## Field Service

The JMS scope of supply xxxxx

Additional service trips and service days are available at an additional cost. Compensation is required for any additional visits caused by site delays that result in the inability to complete field services during scheduled site visits.

Before beginning equipment installation, schedule JMS field service site visits in advance using the contact information provided in this O&M manual. Site visits should be scheduled at least four weeks in advance.

## Scope Exclusions

The following items are excluded from the JMS scope of supply:

- xxxx

## Spare Parts

Please note that a complete table of spare parts is also included on the GA drawings.

- Insert as necessary, otherwise can simply say spare parts aren’t included for this project and remove all this text

# Safety Precautions

Safety must always be considered a basic factor in machinery operation. Most accidents are the result of carelessness or negligence. The following safety instructions are basic guidelines and should be considered as minimum provisions. Please note that not all precautions are applicable to all equipment components. Additional information should be obtained by the purchaser from other sources, including the latest editions of American Society of Mechanical Engineers Standards ANSI B20.1, ANSI B11.0, and ANSI A1264.1, as well as ANSI/ASSP Z244.1-2016.

It is the responsibility of the Contractor, installer, Owner, and user to install, maintain, and operate the equipment components and assemblies manufactured and supplied by JMS in such a manner as to comply with the Williams-Steiger Occupational Safety and Health Act. Furthermore, all parties should comply with all state and local laws and ordinances, as well as the American National Standards Institute Safety Code.

It is extremely important to follow the below precautions to prevent personal injury or property damage:

- Only persons properly trained and familiar with JMS equipment should be permitted to operate or maintain the unit.

- LOCK OUT/TAG OUT ALL POWER prior to any inspection or maintenance.

- Periodically run the equipment for a few minutes to check for excessive vibration, loose fasteners, security of covers and guards, noise, and bearing and gearmotor temperature.

- ALWAYS operate the equipment with covers, guards, and safety labels in place.

- NEVER walk on or across equipment covers, guards, or grating.

- DO NOT place hands, feet, or clothing in equipment openings.

- DO NOT poke or prod the equipment or material in the equipment.

- ALWAYS practice good housekeeping to maintain a clear view of the equipment and all safety devices.

# Delivery, Handling, and Storage

## Upon Equipment Arrival

Although all possible precautions are taken to protect equipment against damage or losses during shipment, before accepting the shipment, check all items against the packing list for shortages and inspect for evidence of physical damage. In either case, immediately notify JMS using the contact information included herein. Keep a record of all claims and correspondence. Photographs are recommended.

As detailed and agreed upon in the original contract and purchase order, all equipment and components delivered to the receiving location should be inspected immediately. A full and complete inspection report noting any visible damage must be transmitted to JMS within ten (10) days of the delivery date. If a written report is not received by JMS within this period, it will be conclusively assumed that the equipment was received in good condition and meets the requirements of the purchase order and/or equipment specification. Failure to submit a full and complete inspection report in the time constraints dictated herein constitutes unqualified acceptance by the buyer or customer, and the buyer or customer waives any rights to rejection or remediation of the delivered equipment.

Do not remove protective covers unless there are indications of damage. Boxes opened for inspection and inventory should be carefully repackaged to ensure protection of the contents, or the parts should be stored in a safe place. Refer to Section 3.3 - Storage. Examine all packing boxes, wrappings, and covers for items that may be attached to them, especially if these items are to be discarded.

## General Handling and Storage Information

Upon completion of the initial inspection, the equipment should be moved from the delivery truck to temporary storage (refer to Section 3.3 - Storage) or immediately installed (refer to Section 4 - Installation Instructions). When maneuvering the equipment, go slowly and use extreme caution. Watch for accidental damage caused during handling and document any issues. It is the responsibility of the handler and installer to ensure that appropriate measures are taken to prevent damage to the equipment during handling and installation.

Provided in the following sections are instructions for handling and storing the equipment. These instructions are intended to cover the basics but will not cover every conceivable situation. Use good judgment when handling and working with the equipment.

### Avoiding Cross-Contamination Between Materials

This equipment is substantially or wholly constructed from corrosion-resistant stainless steel. The Owner and/or installer must protect the equipment against damage to and/or contamination of its protective oxide layer by taking all necessary precautions to prevent the equipment from coming in contact with any carbon steel or carbon steel dust originating from sources outside the immediate system throughout the handling, installation, commissioning, and startup of the system. Failure to protect the equipment from damage to and/or contamination of its protective oxide layer will void the manufacturer’s material warranty.

As a general practice, keep carbon steel components separate from stainless-steel components unless explicitly directed. Avoid stacking components in a manner such that carbon steel and stainless steel will be in unwarranted contact. While not an exhaustive list, protect the equipment from the following forms of carbon steel originating from sources outside the immediate system:

- Truck beds

- Forklifts

- Cables

- Chains

- Tools

- Wire brushes

- Grinding wheels

- Grinding dust

- Nylon lifting straps

If work on any carbon steel components is being performed on site near the storage area for this project, cover stainless-steel components with tarps or paper to protect them from coming in contact with carbon dust particles. If work is being performed indoors, fans should be used to keep carbon steel dust from falling onto stainless-steel components. If work is being performed outdoors, position the work involving carbon steel such that it is located downwind of the stainless-steel component storage area.

Select tools for installation and maintenance of the stainless-steel equipment that are made of stainless or non-magnetic material. Tools made of aluminum bronze, chrome alloys, or stainless alloys are examples of acceptable tool materials. Ensure the tools selected meet the torque requirements for the equipment as detailed on Table 1 in Section 4.1 - Before Installation and the drawings.

Lifting straps previously used for handling carbon steel should not be used to handle stainless-steel equipment components. If there is no method for tracking which material the lifting straps may have handled previously, new lifting straps should be used.

Because a thin layer of chrome oxide naturally forms on the surface of stainless steel, stainless steel resists corrosion. During welding and machining operations, the chrome oxide layer can be damaged. To rebuild this corrosion-resistant layer, pickling and passivation in accordance with ASTM A380 and A967 are conducted on necessary parts of the equipment before it leaves JMS. However, if the corrosion-resistant layer is further breached by installation and/or handling practices, iron particles may be introduced. The introduction of these particles may lead to the appearance of surface corrosion on the stainless-steel component. In the majority of JMS equipment, the surface corrosion is merely aesthetic in nature and does not have any impact on equipment performance. However, these issues can be mitigated or prevented entirely during installation by following the guidance included in this O&M manual.

Some surface corrosion is practically unavoidable over time for most plants due to the environment in which the equipment will be used. Chemicals such as chlorine can introduce corrosion to stainless-steel components without the presence of iron particles, and a damp environment can propagate surface corrosion over time. Most corrosion does not have a performance impact on the equipment over its operational life assuming suitable performance characteristics have been specified. Contact JMS using the contact information provided in this O&M manual if concerns arise about the presence of surface corrosion on JMS equipment.

If surface corrosion is noted on stainless steel and needs to be removed, perform the following steps:

- Clean the affected area thoroughly with a clean rag to remove any moisture on the surface.

- Remove the corrosion from the contaminated area with an abrasive pad that is appropriate for working with stainless steel.

- Treat the abraded area with a local passivation chemical. JMS recommends the use of CitriSurf 2310.

## Storage

Please note that the equipment storage instructions provided herein are the JMS standard requirements for all equipment and cover a variety of components comprehensively. Some instructions may not apply to the equipment covered in this O&M manual. Please disregard any instructions that clearly do not apply. In the case where a vendor O&M manual has been attached to this O&M manual and includes more stringent and/or differing equipment storage requirements, please adhere to the vendor O&M manual instructions. Failure to comply with these equipment storage instructions may void any and all warranties for the equipment.

After the equipment has been checked for any transit damage, JMS recommends the following procedures for equipment storage. Storage refers to the period of time following shipment but prior to installation in which the equipment or component must be protected from damage. For the purposes of this O&M manual, the following requirements are intended to apply when equipment is stored for 30 days or longer on site prior to installation. Requirements may vary based on the duration of the equipment storage.

It is preferred that all equipment be warehoused to protect against inclement weather, dust, and/or damage by vehicles. Similarly, all spare parts should be warehoused until ready for use. Storage inside a building is preferred but covering the equipment or component with a canvas tarp is acceptable unless otherwise indicated. Do not cover the equipment or component with a polyethylene sheet, as this will cause and trap condensation. Additional recommendations for indoor and outdoor storage of various components are highlighted below.

### General Requirements for Indoor Storage

The following general requirements are applicable to all equipment or components stored indoors.

- Store the components in a cool, dry area that is not subject to extreme temperature fluctuations. Protect components from heat and flame, as well as from dirt, mud, and flying debris.

- Ensure the area for storage has adequate ventilation.

- Ensure the storage area ground surface is level.

- If the system includes a Mega-SETTLER, support the plate packs with dunnage in the form of 6” x 6” wood beams to raise them off of the ground and prevent distortion. Always support the plate packs under the vertical uprights in the plate settler truss frame. The individual plates inside the plate pack frame should not under any circumstance contact any part of the dunnage or ground.

- Provide space heaters for heating and drying.

- Provide adequate support under all equipment to prevent distortion and to raise equipment above any undesirable ground or floor conditions. Ensure heavy objects are not stacked on top of the component.

- Ensure tenting and/or tarpaulins (if any) are well supported to provide sufficient ventilation.

- Re-coat parts which may have been scratched or wiped clean of their protective coating in shipment with paint, primer, or grease.

- Shield painted surfaces, including bitumastic coatings, from direct sunlight, which can lead to warping, damage, or chipping.

- Check the equipment periodically for accumulations of moisture and/or surface corrosion and remove. If surface corrosion is present, prepare the surface and re-coat with the proper material. Increase ventilation and reduce humidity.

- In equipment containing moving parts (for which wiring has already been completed and power is available), actuate the equipment through its full range of motion every two weeks.

### General Requirements for Outdoor Storage

The following general requirements are applicable to all equipment or components stored outdoors. It is the responsibility of the Contractor to protect JMS equipment from damage to equipment due to outside storage.

- If warehousing is not possible, choose a site that has adequate drainage, ventilation, and size to maintain space for air circulation and access by inspecting personnel.

- Shield the materials from direct sunlight, rain, snow, dust, etc. with tenting if possible or well-supported tarpaulins at a minimum. Ensure good cover is provided at all times. Ensure that the equipment is protected from contact with other machinery, equipment, etc.

- Provide space heaters for heating and drying in cold or wet weather.

- Use blocks to raise all material off the ground a minimum of 6” higher than any expected level of rain, snow, etc. Components should be stored a minimum of 6” off the ground. If the system includes a Mega-SETTLER, the use of 6” x 6” wood beams is recommended to support and raise the plate packs a minimum of 6” higher than any expected level of rain, snow, etc. Always support the plate packs under the vertical uprights in the plate settler truss frame. The individual plates inside the plate pack frame should not under any circumstance contact any part of the dunnage or ground.

- Provide adequate support of all fabricated steelwork to prevent warping.

- Perform frequent checks to locate surfaces affected by corrosion and accumulations of condensation. It is the responsibility of the Contractor to protect JMS equipment from surface corrosion due to outside storage, including corrosion occurring after the equipment is delivered to the job site but before final finish painting. If surface corrosion is found on painted surfaces, remove the surface corrosion, re-prime, and re-paint the surface. If the surface was originally grease-coated, remove the surface corrosion and re-coat the surface with waterproof grease.

- Block any open inspection doors, etc. slightly to increase ventilation in housings.

- In equipment containing moving parts (for which wiring has already been completed and power is available), actuate the equipment through its full range of motion every two weeks.

### Gear Units

In addition to the general requirements, adhere to the following additional requirements for storage of gear units.

- Although some components are shipped dry, units generally include run-in oils containing surface corrosion-proofing additives. The additives will protect internal gearing for an extended period (see subsequent bullets) under good storage conditions. Verify that the unit is prepared for extended storage with the equipment manufacturer.

- The gear units should remain tightly sealed until startup.

- Store gear units according to the mounting position.

- If the gear unit is packed in containers and shipped with desiccant and a moisture indicator sealed in the plastic wrap, regularly inspect the packaging and humidity indicator. Relative humidity should be less than 50% at all times. The gear unit should be stored under a roof and protected against rain and snow. The unit can be stored for up to 3 years.

- If the gear unit is received open (no packaging), perform regular inspections. Check for cleanness and mechanical damage and inspect the corrosion protection. The gear unit should be stored under a roof and enclosed at a constant temperature and atmospheric humidity (between 41 and 122 degrees F; less than 50% relative humidity). Ensure there are no sudden temperature variations, aggressive vapors, or shocks, and control ventilation with a filter free from dust and dirt. The unit can be stored for 2 years or more.

- In equipment containing moving parts (for which wiring has already been completed and power is available), actuate the equipment through its full range of motion every two weeks.

### Electric Motors and Actuators

In addition to the general requirements, adhere to the following additional requirements for storage of electric motors and actuators.

- Do not remove electrical compartment covers unless specifically instructed in the vendor O&M manual.

- Block open control panel covers or doors so air can circulate.

- Open all cartons and remove all sealing films unless the carton specifically states otherwise. Remove moisture-absorbing materials if found in the cartons. Remove any plastic shock-absorbing particles surrounding the cartons and/or films.

- Store small apparatuses in the original containers (if received dry).

- If not mounted, store motors in the original containers in a clean, dry, and protected warehouse.

- Ensure the storage area is free from vibration and extreme fluctuations in temperature.

- Ensure motors are fully greased.

- Ensure all drains remain fully operable while in storage, and/or remove the drain plugs. The motors must be stored so that the drain is at the lowest point. All breathers and automatic “T” drains must be operable to allow breathing at locations other than through the bearing fits. Motors should be stored in their proper mounting position.

- Where motors are not in the original containers but are instead mounted on other pieces of machinery, the mounting must be such that the drains and breathers are fully operable. The drains must be kept at the lowest point on the motor and/or the drain plugs removed so that all condensation can drain freely.

- Apply corrosion resistant coating to external motor parts when the motor is stored in a corrosive environment.

- Coat all machined parts with Cosmoline (or similar material) if not already coated.

- Connect all units equipped with heaters (if storage conditions in any way simulate or approach operational conditions).

- Keep the motors warm. If the motors are equipped with space heaters, energize them at all times. If space heaters were not supplied, auxiliary heat must be used to keep the motor windings warm and free of condensation.

- If the motor or actuator is installed but not cabled, it is recommended that any plastic transit cable entry plugs are replaced with metal plugs (which are sealed with PTFE tape).

- Check windings for resistance with a megohm meter at the time equipment is put in storage. At termination of storage, repeat this resistance check prior to applying power. The minimum reading should be 1 megohm for motors rated 600 volts or less. Any drop below this point indicates the need for electrical or mechanical drying. When storing a large quantity of motors, perform an inspection of a sample size of the motors by removing the end brackets and visually inspecting for the presence of water in the grease or surface corrosion on the bearing. If water or surface corrosion is present, replace the bearings and re-lubricate.

- Purge grease in the motors at the time of removal from storage, ensuring that an ample supply of fresh grease is in each grease cavity.

- If control panels are provided, adhere to the following additional storage recommendations:

  - If the control panel does not arrive to site wrapped in plastic, wrap the control panel in a covering of heavy-duty plastic or similar material to help prevent the entry of dirt and dust.

  - For control panels not installed and energized immediately, store in a clean, dry place. Maintain a storage temperature between -30 and 65 C (-22 and 149 F). If the storage temperature fluctuates or humidity exceeds 60%, use a space heater to help prevent condensation. If possible, store the control panels in a heated building that offers adequate air circulation and protection from dirt and water.

  - Control panels that are designed for indoor applications do not have sufficient packaging for outdoor storage. If these control panels are to be stored outdoors, install temporary electrical heating to help prevent condensation. Add packaging for protection from the outside elements. A space heater that is rated at 200 watts per section is adequate for the average control panel. Remove all loose packaging and flammable materials before you energize space heaters.

  - Keep dry internally all unenergized control panels for outdoor use by installing temporary heating or energizing optional self-contained space heaters.

# Installation Instructions

## Before Installation

Read the entirety of the provided installation instructions before proceeding with installation. Examine field conditions as early as possible and take field dimensions to confirm that equipment as designed can be installed according to these instructions. Notify JMS immediately if there are undocumented field conditions which are adverse to successful equipment installation. The Contractor must also inspect the latest “APPROVED” or “RELEASED TO FAB” plan and elevation drawings prior to and throughout the installation process.

The following erection and installation procedures are meant to serve as guidelines for installing the JMS equipment and may not address site- or project-specific issues.

If any fit-up problems with equipment are noted during installation, alert JMS immediately using the contact information provided herein. Do not rework any equipment without contacting JMS. Any unauthorized rework will void the warranty on the equipment. JMS reserves the right to have its own personnel or contracted vendors correct field problems. Problems other than minor misfits as defined by AISC 303 should be communicated in writing to JMS using the contact information provided in this O&M manual via the project’s non-conformance reporting procedure.

Throughout the installation procedures described herein, proper industry and plant LOCK OUT/TAG OUT procedures (and confined space entry procedures as necessary) must be followed. These actions protect personnel against electrical and/or mechanical hazards and environments, including asphyxiants.

Please note that all figures depicting the equipment included throughout this O&M manual are for illustrative purposes only and may not reflect the exact conditions or equipment provided for this project. Refer to the drawings for detailed and specific equipment information.

While no special tools are required for working with the Bio-GATE, care should be taken to avoid cross-contamination between carbon steel originating from sources outside the immediate system and stainless-steel components when installing, maintaining, or otherwise working with the equipment or components. Please refer to the additional information about carbon steel contamination provided in Section 3.2.1 - Avoiding Cross-Contamination Between Materials.

Before beginning equipment installation, schedule JMS field service site visits in advance using the contact information provided in this O&M manual. Refer to Section 1 - Scope of Supply for detailed information about what field services are included. Site visits should be scheduled at least four weeks in advance.

Utilize the bolt torque chart provided in Table 1 throughout installation as necessary for general bolt torque values. Do not use impact tools to torque the bolts. Refer to the drawings for unique torque values that may differ from what is provided in Table 1. For 304 stainless steel hardware, refer to the column labeled “18-8 and 316 Stainless Steel”.

Table 1. Typical Bolt Torque Chart

## Detailed Installation Instructions

- Prepare Components for Assembly

  - Refer to the drawings for lifting locations on the Bio-GATE (including any lifting lugs or tabs if provided). Move Bio-GATE using any noted lifting points only to prevent damage to the Bio-GATE.

  - Remove any strapping, wire, or other tethering devices that may have been used during transit from the Bio-GATE.

- Bio-GATE Installation

  - Place the provided gasket between the Bio-GATE flange and the upstream mating flange. The upstream mating flange and associated upstream equipment should be satisfactorily installed according to the separate manufacturer’s instructions prior to installation of the Bio-GATE as described herein.

  - Position the Bio-GATE flange and gasket against the upstream mating flange such that the flanges, gasket, and bolt holes are in alignment.

  - Install the Bio-GATE to the upstream mating flange using the provided hardware.

  - Tighten the hardware according to the bolt torque chart included in Section 4.1 - Before Installation. Verify that the gasket is uniformly compressed between the flanges.

  - [Repeat previous installation Steps 2.a. through 2.d. for the connection on the opposite or downstream side of the Bio-GATE.]

- Actuator Wiring

  - Wire the actuator according to the actuator manufacturer’s installation instructions included in Appendix A: Catalog Cuts.

# Operating Procedures

## General Equipment Operation

The JMS Bio-GATE is designed to aid in maintaining appropriate process flow for wastewater treatment material applications by controlling the release of material to downstream processes. The Bio-GATE may be opened or closed to permit or prevent respectively the distribution of material. When the Bio-GATE is closed, material is temporarily retained and may build in upstream processes. When the Bio-GATE is open, material is transferred to the subsequent downstream process. In applications where multiple Bio-GATEs are used, a combination of open and closed gates may be utilized to specifically direct and distribute material flow based on the current needs and availability of the receiving processes.

Crafted of stainless steel for maximum longevity, the Bio-GATE is carefully and specifically sized and designed for its intended application. The Bio-GATE ensures uniform product distribution and transfer to optimize downstream processes and increase efficiency. The Bio-GATE is capable of transferring a variety of materials, including sludge, grit, and screenings. Note that the Bio-GATE is not designed to be watertight, and the leakage of some water may be expected during normal operation depending on the material being processed.

The Bio-GATE is operated primarily through the use of an electric actuator, but a handwheel is provided on the actuator for manual operation when necessary. Each Bio-GATE is controlled by its own unique actuator.

## Startup

During startup, an operator must be standing by the Bio-GATE and associated component control systems to stop the system in case of emergency. Perform the following procedures:

- Visually inspect the Bio-GATE and any associated equipment for damage. Notify JMS using the contact information provided herein if damage is observed.

- Verify that all preventative maintenance procedures have been completed as directed in Section 6 - Maintenance, Lubrication, & Troubleshooting.

- Verify that all personnel are clear of the equipment and that all obstructions have been removed from the Bio-GATE opening. Do not operate the Bio-GATE until all obstructions have been safely cleared.

- The Bio-GATE may be operated as required via the associated actuator and respective controls. Refer to the actuator manufacturer’s control information provided in Appendix A: Catalog Cuts (as applicable) and/or the associated interlocked equipment controls (not provided herein).

  - Do not overload or otherwise exceed the design parameters and capacities of the equipment outlined in Appendix C: Calculations.

## Shutdown

When it becomes necessary to shut down the equipment, perform the following procedures.

- If possible, allow upstream feed equipment to continue running until all material has been discharged through the open Bio-GATE.

- Shut down all upstream feed equipment according to the appropriate standard operating procedures.

- Close the Bio-GATE via the associated electric actuator or, if not possible, the actuator’s manual handwheel.

- LOTO all power to the Bio-GATE.

- In the event of an emergency, adhere to the LOTO procedures until the source of the emergency condition is properly identified, addressed, and corrected. Do not attempt to turn on the actuators until normal operating conditions are restored.

# Maintenance, Lubrication, & Troubleshooting

While no special tools are required for working with the Bio-GATE, care should be taken to avoid cross-contamination between carbon steel originating from sources outside the immediate system and stainless-steel components when installing, maintaining, or otherwise working with the equipment or components. Please refer to the additional information about carbon steel contamination provided in Section 3.2.1 - Avoiding Cross-Contamination Between Materials.

Please note that not all individual components comprising the Bio-GATE are crafted by JMS (as detailed on the Bill of Materials on the drawings). Although JMS has carefully developed this comprehensive O&M manual to summarize the recommended procedures for effectively maintaining the Bio-GATE and its components as a whole, any and all maintenance, lubrication, and/or troubleshooting procedures from individual component manufacturers for their specific component should supplement or take precedence over the requirements listed herein. Manufacturer reference information, including that which is supplied in Appendix A: Catalog Cuts, should always be referenced during maintenance, lubrication, and troubleshooting procedures where available. If questions arise over the proper maintenance, lubrication, and/or troubleshooting procedures, please contact JMS using the contact information provided in this O&M manual.

## Preventative Maintenance

Before any maintenance or inspection is performed, refer to ANSI/ASSP Z244.1-2016 for minimum safety requirements concerning energy sources.

Practice good housekeeping. Keep the area around the equipment clean and free of obstacles to provide easy access. Establish routine periodic inspections of the equipment to ensure continuous maximum operating performance.

A basic maintenance tool kit is all that is required to maintain this equipment. No special tools are necessary.

Table 2. Bio-GATE Preventative Maintenance

| Component | Recommended Maintenance | Frequency |
| --- | --- | --- |
| General | Inspect slide gate for material buildup. Dislodge and clean material from the slide gate as required. | Daily |
| Hardware | Inspect all bolts associated with the Bio-GATE (particularly around the mating flanges) and secure any that are loose. Refer to the guidance provided in Section 4 - Installation Instructions regarding proper hardware tightening. | Quarterly |
| Seals | Inspect slide gate seals for wear. This is often evidenced by the excessive leakage of water and/or more substantial material. Note that the Bio-GATE is not designed to be watertight, so the appearance of a reasonable amount of water is acceptable during normal operation. Replace the seals as required according to the directions provided in Section 6.2.1 - Seal Replacement. | Quarterly |
| Actuator | Test actuator limit switches according to the instructions provided in the manufacturer’s information included in Appendix A: Catalog Cuts. Adjust limit switches as needed, again referencing the actuator information included in Appendix A: Catalog Cuts. | Annually or as needed if gate is not seating correctly when fully opened or closed. |
|  | Refer to the manufacturer’s maintenance information provided in Appendix A: Catalog Cuts for preventative maintenance procedures related to the actuator. | Refer to the maintenance intervals provided in the actuator manufacturer’s information included in Appendix A: Catalog Cuts. |
| [Non-Rising Stem Bearing | Lubricate the bearings according to the information provided in Section 6.3 - Lubrication. | Refer to the maintenance interval provided in Section 6.3 - Lubrication.] |

## Corrective Maintenance

### Seal Replacement

If it has been determined that the Bio-GATE seals require replacement, perform the following procedures. It is recommended that all four seal sections are replaced at one time. If possible, replace the seals while the Bio-GATE is closed to ensure the best possible seating of the seal.

  - Order and obtain replacement seals from JMS using the contact information provided herein.

  - Once the replacement seals are available, LOTO all power to the Bio-GATE.

  - Remove the hardware and any retainers holding the worn seals in place.

  - Remove the worn seals.

  - Refer to the drawings included in Appendix B: Equipment Drawings to confirm on which sides of the Bio-GATE the two different lengths of seals should be installed.

  - Working with one seal section at a time, position the new seal such that the bolt holes in the seal are aligned with the holes on the Bio-GATE frame.

  - Working with one seal section at a time, loosely install the hardware and any retainers on top of the seal and onto the Bio-GATE frame.

  - Use a small block of wood or similar tool to gently and carefully tap the seals such that they contact the closed Bio-GATE (or will contact the Bio-GATE when fully closed if this procedure is being performed with the Bio-GATE in the open position). This ensures an effective seal. Avoid tapping the retainers (if provided).

  - Tighten the hardware according to the information provided in Table 1 within Section 4.1 - Before Installation. Verify that all seals are snugly and properly seated between the retainer and the Bio-GATE frame.

## Lubrication

Refer to the actuator manufacturer’s supplemental information provided in Appendix A: Catalog Cuts for necessary actuator lubrication requirements (if any).

[Lubricate the bearing associated with the actuator’s non-rising stem according to the manufacturer’s information provided in Appendix A: Catalog Cuts.]

## Troubleshooting

Table 3. Bio-GATE Troubleshooting

| Problem | Probable Cause | Solution |
| --- | --- | --- |
| Bio-GATE not opening or closing when desired | Bio-GATE is not receiving “OPEN” or “CLOSE” signal from controls | Verify that a signal is being sent from the control panel. Refer to the actuator manufacturer’s control information included in Appendix A: Catalog Cuts (as applicable) and/or the associated interlocked equipment controls (not included herein). |
|  |  | Verify that the signal is being received by the Bio-GATE actuator. |
|  | Limit switches are not properly set | Refer to the actuator manufacturer’s instructions included in Appendix A: Catalog Cuts for information on how to properly reset the limit switches. |
|  | Bio-GATE actuator is tripping out on over torque | Remove the dust cover from the Bio-GATE and inspect for blockages in the gate. If no blockages are observed, incrementally increase the actuator torque output (up to a maximum of 60% of the actuator’s total torque output value). Refer to the actuator manufacturer’s instructions included in Appendix A: Catalog Cuts for detail. |
|  | No power at the actuator | Utilize a certified electrician to verify that power is being conveyed to the motor and back to the source. |
|  | Actuator failure | Notify JMS using the contact information provided in this O&M for recommended procedures. |
| Bio-GATE leaks water excessively (or leaks other more substantial material) when closed Note that the Bio-GATE is not designed to be watertight, and the leakage of some water may be expected during normal operation depending on the material being processed. | Seals are worn, torn, or out of alignment | Remove the dust cover and inspect the seals while the Bio-GATE is in the closed position for abnormalities or wear. Then observe the seals while the Bio-GATE is in operation for abnormalities or wear. Replace or adjust seals to accommodate proper operation as required. Details regarding seal replacement are included in Section 6.2.1 - Seal Replacement. |
|  | Bio-GATE is not fully closed | Remove the dust cover and observe the Bio-GATE in operation. Clear any blockages. The Bio-GATE should be seated approximately 1-1/2” beyond (or under) the end seal when fully closed. Adjust the limit switches if required using the detailed actuator manufacturer information provided in Appendix A: Catalog Cuts. |
|  | [Bio-GATE drain is clogged | Carefully clean the Bio-GATE drain, removing any material buildup or debris.] |
| Material bridges at the Bio-GATE (i.e. collects on top of the gate and prevents material from passing through) | Bio-GATE is not fully opening | Remove the dust cover and observe the Bio-GATE in operation. Clear any blockages. The Bio-GATE should be positioned approximately 1-1/2” beyond the seal when fully opened. Adjust the limit switches if required using the detailed actuator manufacturer information provided in Appendix A: Catalog Cuts. |

# Policies

## Warranty

All JMS equipment and/or materials are of high quality and are manufactured in conformity with the best commercial practices. JMS guarantees all equipment and materials manufactured or supplied by JMS to be free from defects in material and workmanship at the time of startup for a period of XXXXX. JMS will furnish without charge but will not install replacements for such parts and materials JMS finds to be defective.

This guarantee does not apply to any equipment which has been improperly handled or stored, improperly lubricated, subjected to misuse or neglect, misapplied with reference to the Engineer's Specifications, altered or tampered with, and/or damaged by corrective work performed without JMS’ specific written consent. No allowances will be made for such corrective work done without such consent.

Deterioration by chemical action, improper maintenance, or normal wear does not constitute defects and are therefore not covered by this warranty. Additionally, consumable items are not covered by this warranty. All warranty claims must be submitted within ten (10) calendar days of discovery of defects or they will be deemed waived. The foregoing is in lieu of all other warranties, whether expressed or implied.

## Liability

It is expressly understood that JMS’ liability for JMS products is limited to the furnishing of such replacement parts, and that JMS will not be liable for any other expense, injury, loss, or damage, whether direct or consequential, including but not limited to loss of profits, production, or increased cost of operation arising in connection with the sale or use of, or inability to use, JMS equipment and/or materials for any purpose except as herein provided.

In the event a customer's order form states any liability terms which are additional to or different from these set forth herein, this form must be acknowledged in writing by JMS to accept any liability set forth in such form(s).

## Returns

All returns must be authorized by JMS, and no credit will be allowed for returned items that are damaged in transit, incomplete, or received in an unsatisfactory condition. All items that are not eligible for credit will be returned to customer via freight collect or discarded upon customer's instructions.

## Delivery

Delivery dates represent only JMS’ best estimate of the time required to complete the work and ship the material from JMS’ plant. All orders are accepted with the understanding that shipping dates are approximate and subject to change because of factory conditions, fires, strikes, material shortages, civil or military authority, acts of God, or other causes beyond JMS knowledge or control.

Back charges against JMS for alterations, shortages, damage repair, and/or discrepancies will be accepted only with written prior approval from a duly authorized representative of JMS.

## Thread Lubricant Information

All JMS bolts and anchors are stainless steel material unless otherwise specified. Without an application of thread lubricant, bolting materials may become locked together. JMS strongly recommends the use of NSF-61 approved thread lubricant on all stainless steel bolts and anchors.

## Standard Erecting Practices

All fabricated equipment manufactured by JMS is shop checked for accuracy before shipment and should not present any erection problems. Due to specific field conditions, a reasonable amount of fit-up is considered standard erection practice. The use of tools such as “come-a-longs”, jacks, drift pins, and reamers is to be expected.

Standard erecting practice as defined by the AISC “Code of Standard Practice”, Section 7.14, states the following:

“The correction of minor misfits by moderate amounts of reaming, grinding, welding, or cutting, and the drawing of elements into line with drift pins shall be considered to be normal erection operations. Errors that cannot be corrected using the foregoing means, or that require major changes in member or connection configuration, shall be promptly reported to the ODRD, the ODRC, and the fabricator, by the erector, to enable the responsible entity to either correct the error or approve the most efficient and economical method of correction to be used by others.”

If a problem is traceable to JMS fabrication or engineering, JMS will work with you to resolve this problem. Back charges for replacing or correcting materials require prior written approval of an authorized JMS representative. The back charges will only be considered with prompt, complete cost documentation based on standard direct field labor hours and materials. Profit, overhead, and any other charges will not be allowed. Payment may be refused for corrective work without prior approval.

Problems other than minor misfits as defined by AISC 303 should be communicated in writing to JMS using the contact information provided in this O&M manual via the project’s non-conformance reporting procedure.

Appendix A: Catalog Cuts

Appendix B: Equipment Drawings

Appendix C: Calculations

Appendix D: Startup Reports

PLACEHOLDER

Startup reports will be completed and made available as appropriate.

Appendix E: Controls

Refer to the actuator manufacturer’s control information included in Appendix A: Catalog Cuts (as applicable) and/or the associated interlocked equipment controls (not included herein).

Appendix F: O&M Revision History

| Date | Rev. | Description of Change | Author |
| --- | --- | --- | --- |
| INSERT DATE MM/DD/YYYY | 0 | Initial release. | INSERT INITIALS |